PLC-Based Predictive Maintenance System for Water Pumping Industry Using IoT

Aniruddha Nemade, Khushi Sawalkar, Ruchi Parekar, Vinayak More, Nestor Philips

Department of Electronics and Telecommunication Engineering

JSPM's Rajarshi Shahu College of Engineering, Tathawade, Pune, India

Email: parekarruchi@gmail.com

Abstract: Water pumps play an essential role in the basic operation of a manufacturing plant, even if we rarely realise this until it fails, and occasionally without warning; their immediate impact is non-existent. Most places use corrective maintenance, fixing a pump only after it breaks, or preventative maintenance by servicing it at set times for no reason. Neither method reliably catches the slow, gradual degradation that so often precedes a failure. In this paper, we introduce PLC-based predictive maintenance for monitoring the health status of industrial water pumps, using current, temperature, vibration, and speed sensors to obtain a fuller picture of pump health. An ESP32 module collects readings from sensors, compares them with threshold values in real time, and sends them to a cloud dashboard. Metrics stored in the dashboard maintain historical data and help detect trends indicating slow degradation, assisting with predictive maintenance decisions. The system continues to monitor whilst readings are still within limits, but when a critical condition is detected the ESP32 sends a command to a Programmable Logic Controller (PLC) which stops the pump and records an alert, fault indication and data logging ahead of the dangerous condition manifesting itself as failure, providing time for maintenance staff to respond. The system identified developing faults knowledgably before it was unavoidable in time, leading to an improvement in maintenance planning, reduced downtime and extended pump service life. The design is low-cost and easy to scale, making it ideal for several water-pumping tasks- and shows how Industry 4.0 tools can assist with simple factory operations.

Keywords— Predictive Maintenance, PLC, ESP32, IoT, Industrial Automation, Water Pump, Vibration Monitoring, Current Sensor, Temperature Monitoring, Cloud Computing.

I. Introduction

Water pumping systems form the backbone of many essential operations. Industrial plants, municipal water supply networks, farm irrigation and wastewater treatment facilities all depend on them. These systems are expected to run continuously because any interruption disrupts the processes and communities that rely on them. In practice pumps do not always behave as expected. Wear on mechanical parts, motor faults and a range of other issues push a pump toward failure gradually or suddenly. Warning signs are often minimal and there is little time to react once a fault begins.

Pumps have traditionally been kept running in one of two ways. Corrective maintenance addresses a fault only after it happens. The pump runs until something breaks and repairs follow in response. Preventive maintenance takes a more proactive stance and schedules repairs at fixed time intervals regardless of the pump's actual condition. This lowers the chance of sudden breakdowns but brings its own drawback. Equipment that is still working normally often gets serviced anyway simply because the schedule calls for it. The result is wasted resources and downtime that could have been avoided. This trade-off has pushed the industry toward predictive maintenance instead. Predictive maintenance tracks a pump's actual condition over time and catches developing problems before they turn into major failures.

This shift has become possible largely because of recent progress in the Internet of Things (IoT), cloud computing and industrial controllers. Together these technologies support intelligent maintenance systems that can watch over equipment around the clock. Once sensors are connected with controllers and cloud platforms continuous tracking of key parameters such as current draw, vibration and temperature becomes practical and affordable. This makes earlier fault detection possible and allows remote diagnosis so engineers no longer need to be at the site in person.

This work addresses that need directly. Sensors connected to a controller collect real-time operating data as the pump runs. This data is then sent to a monitoring platform where it can be viewed and analyzed giving operators a clear picture of the pump's condition at any moment. The resulting system is more reliable, less prone to unplanned downtime, cheaper to maintain and better aligned with the predictive maintenance strategies now spreading across the water pumping industry under Industry 4.0.

II. Research Gap and Motivation

A. Research Gap

Some predictive maintenance systems already exist for industrial equipment but most rely on a single parameter such as motor current, vibration or temperature as the primary indicator of health. This is a limitation. Equipment failures are rarely caused by one factor in isolation. They typically arise from several operating conditions interacting at the same time so a single-parameter view only captures part of the picture. Many existing systems also depend on periodic inspection rather than continuous monitoring so faults are often caught later than necessary sometimes only after the equipment has already failed.

A similar gap exists on the software side. IoT-based monitoring platforms are good at collecting sensor data but generally offer limited decision-support capability. PLC-based systems present the opposite trade-off. They offer reliable industrial automation but rarely include cloud connectivity, remote diagnostics or predictive analytics. Without multi-sensor monitoring combined with some form of intelligent analysis maintenance stays largely reactive and ends up costing more than it should.

What is missing is a system that brings together industrial-grade PLC control, IoT-based remote monitoring, multi-parameter condition monitoring and a degree of intelligent fault analysis into a single framework capable of improving equipment reliability and reducing downtime.

B. Motivation

As industries move toward uninterrupted operation predictive maintenance has become a core part of Industry 4.0 rather than an optional addition. An unexpected pump failure does not just halt production. It also tends to drive up repair costs and energy use.

This work is motivated by the need for a predictive maintenance system that is technically capable and affordable to deploy while giving continuous real-time visibility into the pump parameters that matter most. Combining a PLC with an ESP32 IoT gateway and cloud services enables early fault detection, remote monitoring and maintenance alerts issued while there is still time to act. In practice this means better equipment reliability, longer service life, lower maintenance costs and maintenance planning driven by data rather than fixed schedules.

III. Literature Review

TABLE I. LITERATURE SURVEY

| Ref. | Existing Work | Limitation | Proposed Improvement |
| --- | --- | --- | --- |
| [1] | Lee et al. (2019) — IoT-based motor monitoring | Only current monitoring | Multi-sensor health monitoring |
| [2] | Wang et al. (2020) — Vibration-based fault detection | Cannot detect electrical faults | Combines vibration and electrical parameters |
| [3] | Patel et al. (2021) — PLC automation for pump control | No cloud connectivity | PLC with IoT integration |
| [4] | Sharma et al. (2022) — Temperature monitoring | No predictive analytics | Intelligent fault prediction |
| [5] | Kumar et al. (2023) — Remote monitoring dashboard | Limited industrial automation | Industrial PLC + IoT architecture |

A review of the literature shows most predictive maintenance systems monitor only one or two machine parameters. This limits how accurate the overall health assessment can be. Current-based methods detect overload conditions well but cannot pick up mechanical faults such as bearing wear or shaft misalignment. Vibration analysis suits mechanical fault detection instead but gives no information about electrical problems.

IoT-based monitoring systems offer remote access to machine data and make continuous monitoring easier. They often lack the reliability and real-time control industrial applications need though. PLC-based automation systems provide dependable machine control and real-time operation but usually come with limited cloud connectivity and few predictive maintenance features.

These observations point to one conclusion. Better predictive maintenance comes from combining PLCs, IoT communication, cloud monitoring and multi-sensor condition monitoring within a single system. The approach proposed in this paper follows that idea and brings current, vibration, temperature and speed monitoring together into one architecture. This allows real-time fault detection while also supporting remote monitoring.

IV. Novel Contributions of the Proposed System

The main contributions of this work are summarized below:

- Development of a PLC-based predictive maintenance system for industrial water pumps.

- Integration of current, vibration, temperature and speed sensors to monitor the overall health of the equipment.

- Real-time pump protection through PLC-controlled shutdown triggered by fault detection using the ESP32.

- IoT-based remote monitoring using an ESP32 gateway and a cloud platform.

- Early fault detection and predictive maintenance alerts based on continuously monitored sensor data.

- A scalable and cost-effective system built for Industry 4.0 industrial applications.

- Reduced equipment downtime, maintenance costs and unexpected pump failures through continuous condition monitoring.

V. Proposed System

The proposed system continuously monitors the operating condition of industrial water pumps and catches possible faults before they lead to failure. It combines industrial automation with IoT using a Programmable Logic Controller (PLC), condition-monitoring sensors, an ESP32 communication module and a cloud-based monitoring platform.

The sensors send their readings to the ESP32 module. The ESP32 continuously reads the sensor data and compares the values against predefined thresholds. It also uploads the readings to a cloud dashboard. The dashboard stores the collected data and analyzes trends over time to spot gradual changes in pump condition and support predictive maintenance. As long as the readings stay within normal limits monitoring continues without interruption. If a critical condition is detected the ESP32 sends a stop command to the PLC. The PLC then shuts down the pump while the system generates an alert, records the fault and logs the related data.

Unlike conventional monitoring systems that usually depend on a single parameter the proposed system monitors motor current, bearing temperature, vibration level and shaft speed at the same time. Using these parameters together gives a more complete picture of the pump's condition and helps catch faults at an early stage. This lets maintenance decisions be based on the pump's actual condition rather than waiting for a failure to happen.

The proposed system provides the following functions:

- Continuous monitoring of the operating parameters of the water pump.

- Real-time industrial control using a PLC.

- Remote monitoring through IoT-based cloud connectivity.

- Early fault detection using threshold-based condition monitoring.

- Automatic alarm generation and maintenance notifications when faults are detected.

- Storage of historical operating data for trend analysis and maintenance planning.

- Improved equipment reliability with lower downtime and reduced maintenance costs.

VI. System Architecture

The proposed system is divided into four main layers.

1. Data Acquisition Layer

The data acquisition layer collects real-time operating data from the water pump. A set of sensors is installed on the pump and motor to continuously monitor their operating condition. The monitored parameters include:

- Current consumption (Current Transformer Sensor)

- Motor temperature (MAX6675 with K-Type Thermocouple)

- Motor vibration (MPU6050 Accelerometer)

- Motor speed (Speed Sensor)

These sensors continuously send machine condition data to the ESP32, giving the system the information it needs for monitoring and fault detection.

2. Control Layer

The PLC receives commands from the ESP32 to protect the water pump during operation. Its main responsibilities include:

- Receiving stop commands from the ESP32.

- Stopping the water pump motor when a fault is detected.

- Executing the required industrial control logic.

- Operating alarms and protection relays.

PLCs are built for industrial applications and offer reliable operation, quick response and steady performance under demanding operating conditions.

3. IoT Communication Layer

The ESP32 acts as the central processing unit of the proposed system. It reads sensor data, analyzes the operating conditions and manages communication with the cloud platform. Its main functions include:

- Reading data from the sensors.

- Comparing sensor readings with predefined threshold values.

- Sending a stop command to the PLC when a critical condition is detected.

- Formatting sensor data for transmission.

- Uploading data to the cloud server.

- Providing remote monitoring through Wi-Fi.

- Sending maintenance alerts to operators.

This layer lets maintenance engineers monitor the condition of the water pump remotely from any location with an internet connection.

4. Cloud Monitoring Layer

The cloud platform receives data from the ESP32, stores it and displays it in a user-friendly format. It provides the following features:

- Real-time dashboard for monitoring system performance.

- Historical trend analysis of sensor data.

- Equipment health monitoring.

- Alarm history for recorded fault events.

- Maintenance reports.

- Remote access through web and mobile devices.

The cloud platform also stores historical operating data, making it possible to study long-term performance trends. This information supports predictive maintenance by helping spot changes in equipment condition over time.

VII. Working Principle

In operation, the system follows this sequence:

1. The industrial water pump is switched ON.

2. Current, vibration, temperature and  speed sensors continuously monitor machine health.

3. Sensor signals are transmitted to the ESP32, which reads the sensor data.

4. The ESP32 compares each parameter against predefined threshold values and uploads the sensor data to the cloud dashboard, which stores it and performs trend analysis.

5. If all parameters remain within acceptable limits, the ESP32 continues monitoring.

6. If a critical condition is detected, the ESP32 sends a stop command to the PLC.

7. The PLC stops the water pump.

8. The system generates an alert and fault indication and  logs the event.

9. The ESP32 simultaneously uploads sensor readings to the cloud platform.

10. Maintenance personnel can remotely monitor equipment status using a web dashboard.

11. Historical sensor data are stored for trend analysis and predictive maintenance planning.

VIII. System Component Architecture

To illustrate the system's physical and logical layout, a component diagram was developed, shown in Fig. 1.

Fig. 1. Component Diagram of the Proposed System

As shown in the diagram, the temperature, vibration, current and  speed sensors feed into the ESP32 module, which reads the sensor data and performs threshold comparison locally. The ESP32 communicates wirelessly (Wi-Fi/HTTP) with a Node.js-based backend server for continuous data logging and dashboard visualization, where historical data is stored and trend analysis is performed to identify gradual degradation. Separately, over serial/digital I/O, the ESP32 sends a stop command to the PLC whenever a critical condition is detected. The PLC then stops the pump and triggers the alarm and fault-indication signals and updates the backend server over Modbus/RS-485. The backend server writes data to a MongoDB database and drives the web-based monitoring dashboard. Together, this provides a clear structural view of the system, from sensor-level data acquisition to the communication between individual hardware components.the way down to how the individual hardware components talk to one another.

IX. Hardware and Software Requirements

A. Hardware Requirements

The system is built from industrial-grade hardware selected to withstand harsh industrial environments. The hardware configuration includes sensors for condition monitoring, an ESP32 module for data acquisition, threshold analysis and  IoT communication, a PLC that executes pump shutdown on command and  a cloud dashboard for historical storage, trend analysis and  remote monitoring.

TABLE II. HARDWARE SPECIFICATIONS

| Component | Specification | Purpose |
| --- | --- | --- |
| PLC | Mitsubishi FX Series PLC | Pump shutdown execution and protection |
| ESP32 | Dual-Core Wi-Fi Microcontroller | IoT communication |
| Current Sensor | Current Transformer (CT) Sensor | Motor current monitoring |
| Temperature Sensor | MAX6675 with K-Type Thermocouple | Motor temperature monitoring |
| Vibration Sensor | MPU6050 | Bearing and shaft vibration analysis |
| Speed Sensor | Hall Effect / IR Speed Sensor | Shaft RPM measurement |
| Relay Module | 24 V Industrial Relay | Pump protection |
| Water Pump | Single Phase / Three Phase Motor | Experimental setup |
| Power Supply | 24 V DC | System power |
| Wi-Fi Router | IEEE 802.11 b/g/n | Internet connectivity |

The software configuration draws on industrial automation software, embedded programming tools, cloud services and  data visualization platforms.

On the software side, the setup draws on industrial automation software, embedded programming tools, cloud services and  data visualization platforms.

TABLE III. SOFTWARE SPECIFICATIONS

| Software | Purpose |
| --- | --- |
| GX Works3 / GT Designer3 | PLC and HMI Programming |
| Arduino IDE | ESP32 Programming |
| Node.js / MongoDB | Backend Server and Cloud Database |
| MQTT Protocol | IoT Communication |
| Python | Data Processing (Optional) |
| Microsoft Excel | Data Analysis |
| Windows 10/11 | Development Environment |

A laboratory-scale water pumping system was built for testing, integrating a PLC, an ESP32 and  the full sensor suite. The ESP32 continuously reads the current, temperature, vibration and  speed sensors mounted on the pump motor, compares the readings against programmed threshold values and  transmits the data to the cloud dashboard over Wi-Fi, where it is stored and analyzed for trends.

Testing covered several operating conditions, including normal operation, overload, excessive vibration and  motor overheating, with threshold values programmed into the ESP32 to recognize abnormal readings. Whenever a monitored parameter exceeded its safe limit, the ESP32 sent a stop command to the PLC, which shut down the pump and activated the protective relay to prevent equipment damage, while the ESP32 continued uploading live sensor readings and the resulting alert and fault indication to the cloud dashboard, making the abnormal condition visible for remote monitoring and maintenance planning.

Overall, the system performed reliably, demonstrating continuous monitoring, real-time fault detection and  remote visualization of the pump's health parameters.

Overall, the setup held up well, demonstrating continuous monitoring, real-time fault detection and  remote visualization of the pump's health parameters.

Fig. 2. Laboratory-Scale Experimental Test Setup — PLC Panel, VFD and  Motor Under Test

Fig. 3. Sensor Analytics and Trends Dashboard Showing Temperature, Vibration, Current, Speed and  Health Index

The system was evaluated across a range of operating conditions while sensor data was collected continuously, in order to assess its monitoring and fault-detection performance. Throughout testing, the ESP32 consistently identified abnormal conditions by comparing live measurements against the configured threshold values and reliably commanded the PLC to stop the pump when required.

The use of multiple sensors improved fault-detection accuracy compared with a single-parameter approach. Cloud-based monitoring allowed maintenance staff to check equipment status remotely and  the PLC consistently executed the pump shutdown commands issued by the ESP32 to protect the equipment.

Pulling in multiple sensors clearly paid off in fault-detection accuracy compared to a single-parameter system. Meanwhile, cloud-based monitoring meant maintenance staff could check equipment status without being on site and  the PLC reliably executed the pump shutdown commands issued by the ESP32 to protect the equipment.

TABLE IV. PERFORMANCE ANALYSIS UNDER DIFFERENT OPERATING CONDITIONS

| Operating Condition | Current | Temp. | Vibration | Speed | Status |
| --- | --- | --- | --- | --- | --- |
| Normal Operation | Normal | Normal | Normal | Normal | Healthy |
| Overload | High | Normal | Normal | Reduced | Warning |
| Bearing Fault | Normal | Slightly High | High | Normal | Maint. Req. |
| Motor Overheating | High | High | Normal | Reduced | Critical |
| Combined Fault | High | High | High | Low | Shutdown |

TABLE V. PERFORMANCE SUMMARY

| Parameter | Result |
| --- | --- |
| Real-Time Monitoring | Yes |
| PLC Response Time | < 100 ms |
| Cloud Update Interval | 1–2 s |
| Fault Detection | Real-Time |
| Remote Monitoring | Supported |
| Predictive Maintenance | Enabled |

Fig. 4. Real-Time Monitoring and SCADA Control Dashboard During Testing

XII. Advantages of the Proposed System

•  Continuous monitoring of critical pump parameters.

•  Early detection of mechanical and electrical faults.

•  Reduction in unplanned equipment downtime.

•  Lower maintenance and operational costs.

•  Remote monitoring through IoT technology.

•  Improved equipment reliability and service life.

•  Industrial-grade PLC-based control for high reliability.

•  Scalable architecture suitable for Industry 4.0 applications.

XIII. Applications

•  Water Treatment Plants

•  Municipal Water Distribution Systems

•  Industrial Pumping Stations

•  Chemical Processing Industries

•  Oil and Gas Industries

•  Agricultural Irrigation Systems

•  Power Plants

•  Manufacturing Industries

•  Smart Factories

•  Industrial Automation Systems

This paper presented a PLC-based predictive maintenance system for the water pumping industry that combines industrial automation, multi-parameter condition monitoring AND CLOUD-based remote monitoring within a single framework. Dedicated sensors connected to an ESP32 module continuously monitor motor current, temperature, vibration and  rotational speed. The ESP32 compares these readings against threshold values and streams the data to a cloud dashboard, which stores it and performs trend analysis. When the ESP32 detects a critical condition, it sends a stop command to a PLC, which shuts down the pump and raises an alert, allowing maintenance personnel to review equipment status and long-term 3trends remotely.

Testing confirmed that the system reliably detected abnormal operating conditions before they developed into failures, reducing downtime and maintenance costs while improving overall pump reliability. Its modular architecture, industrial-grade control and  IoT connectivity make it well suited to modern Industry 4.0 environments and smart manufacturing systems more broadly.

Testing backed this up: the system reliably caught abnormal operating conditions before they turned into failures, which is exactly what brings down downtime and maintenance costs while making the pump more reliable overall. Between the modular architecture, industrial-grade control and  IoT connectivity, the design is a natural fit for modern Industry 4.0 environments and smart manufacturing systems more broadly.

The system can be extended in several directions, including:

There is also plenty of room to build on this system further, particularly by incorporating:

•  Machine Learning models for fault prediction.

•  Artificial Intelligence-based Remaining Useful Life (RUL) estimation.

•  Digital Twin technology for real-time equipment simulation.

•  Edge AI implementation for local predictive analytics.

•  MQTT and OPC UA protocols for industrial communication.

•  SCADA integration for centralized monitoring and control.

•  Mobile application with instant fault notifications.

•  Cloud-based analytics dashboards for multiple pumping stations.

•  Energy consumption optimization using AI algorithms.

•  Integration with Computerized Maintenance Management Systems (CMMS).

References

[1] Lee, J. et al., "IoT-based motor monitoring for industrial equipment," 2019.

[2] Wang, Y. et al., "Vibration-based fault detection in rotating machinery," 2020.

[3] Patel, R. et al., "PLC automation for pump control systems," 2021.

[4] Sharma, A. et al., "Temperature-based condition monitoring of industrial motors," 2022.

[5] Kumar, S. et al., "Remote monitoring dashboard for industrial equipment," 2023.